GYPSUM BOARD SHAFT WALL SYSTEMS - SECTION 09260 / 09 21 16.23

*****************************************************************

Use this guide specification to specify gypsum drywall Shaft Wall systems by U.S. Gypsum Co., incorporating specially shaped light gage steel framing members for construction of fire-rated partitions enclosing elevator shafts, mechanical shafts, stairways, etc.  Review a copy of USG publication SA-926 before editing this specification.

*****************************************************************

Use the following for ALL Systems.  Re-number and re-letter after making all selections.  Delete all bolded instructions.  ********

PART 1 GENERAL

1.01 SECTION INCLUDES

A. Tested and rated gypsum board/steel stud enclosures for stairways, vertical and horizontal duct enclosures, and soffits.

1.02 REFERENCES

- ASTM A653/A653M: Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

- ASTM C475: Standard Specification for Joint Compound and Joint Tape for Finishing Gypsum Board

- ASTM C645: Standard Specification for Nonstructural Steel Framing Members

- ASTM C665, Type I: Standard Specification for Mineral-Fiber Blanket Thermal Insulation for Light Frame Construction and Manufactured Housing

- ASTM C840: Standard Specification for Application and Finishing of Gypsum Board.

- ASTM C919: Standard Practice for Use of Sealants in Acoustical Applications

- ASTM C954: Standard Specification for Steel Drill Screws for the Application of Gypsum Panel Products or Metal Plaster Bases to Steel Studs from 0.033 in. (0.84 mm) to 0.112 in. (2.84 mm) in Thickness

- ASTM C1002: Standard Specification for Steel Self-Piercing Tapping Screws for the Application of Gypsum Panel Products or Metal Plaster Bases to Wood Studs or Steel Studs.

- ASTM C1325: Standard Specification for Non-Asbestos Fiber-Mat Reinforced Cementitious Backer Units

- ASTM C1396: Standard Specification for Gypsum Board

- ASTM C1658: Standard Specification for Glass Mat Gypsum Panels

- ASTM D3273: Standard Test Method for Resistance to Growth of Mold on the Surface of Interior Coatings in an Environmental Chamber.

- ASTM E84: Standard Test Method for Surface Burning Characteristics of Building Materials.

- NFPA 252: Standard Methods of Fire Tests of Door Assemblies

1.03 DEFINITIONS

A. Shaft Wall: An assembly of steel framing, gypsum panels, and other materials used to enclose stairways, elevator shafts, duct shafts used for air supply and return, and shafts housing mechanical and electrical components.

1. Shaft wall assemblies must have passed successfully fire and sound tests performed by recognized testing laboratories.

2. When utilizing additional layers of the same gypsum boards used in the fire and sound tests, a shaft wall assembly may be estimated to have a higher fire resistance rating than that of the basic test.

B. Adhere: Fasten with adhesive.

C. Attach: Fasten with steel screws, power-driven or non-power-driven.

D. Ductside - That side of a shaft wall that used as a duct or vent in which pressurized air flows.

E. Floorside: That side of a shaft wall that has a floor upon which people may stand.

F. Horizontal: Long dimension of board perpendicular to studs.

G. Inside: That space between studs and between inside faces of inner board faces.

H. Position: Place without attaching or adhering.

I. Roomside: That surface of a duct or shaft which is in a room or space.

J. Shaftside: That side of shaft wall that does not have floor upon which people may stand (such as an elevator shaft, airway, and the like), but which may contain a landing(s) (such as a stairway).

K. Vertical: Long dimension of board parallel with studs.

L. Abbreviations:  See Section 01092-Abbreviations.

1.04 SYSTEM DESCRIPTION

******** Select one or more of the following Systems.  Delete those not selected.  ********

A. Vertical Shaft Wall Assembly; System A:

1. UL Design U415, 1 hr.  Framing - steel studs 24 in. oc. Shaftside - vertical liner panels positioned into studs; floorside - vertical gypsum face boards attached to studs.

A. Vertical Shaft Wall Assembly; System A:

1. UL Design U469, 1 hr.  Framing - steel studs 24 in. oc. Shaftside - vertical liner panels positioned into studs; floorside - vertical gypsum face boards attached to studs.

A. Vertical Shaft Wall Assembly; System B:

1. UL Design U438, 2 hr, STC 39.  Framing - steel studs 24 in. oc.  Shaftside - vertical liner panels positioned into studs; floorside - vertical gypsum base boards attached to studs, vertical gypsum face boards attached to studs through base boards.

A. Vertical Shaft Wall Assembly; System B:

1. UL Design U438, 2 hr, STC 47.  Framing - steel studs 24 in. oc.  Shaftside - vertical liner panels positioned into studs; floorside - vertical gypsum base boards attached to studs, vertical gypsum face boards attached to studs through base boards; inside - sound insulation friction-fit between studs.

A. Vertical Shaft Wall Assembly; System C:

1. UL Design U492, 2 hr, STC 52.  Framing - steel studs 24 in. oc.  Shaftside - vertical liner panels positioned into studs; floorside - vertical gypsum face boards attached to studs through base boards; inside - sound insulation friction-fit between studs

A. Vertical Shaft Wall Assembly; System D:

1. UL Design U459, 2 hr.  Framing - steel studs 24 in. oc.  Shaftside - vertical liner panels positioned into studs; floorside - vertical gypsum base boards attached to studs, vertical cement face boards adhered to base boards and attached to studs through base boards; inside - sound insulation friction-fit between studs.

A. Vertical Shaft Wall Assembly; System E:

1. UL Design U467, 2 hr.  Framing - steel studs 24 in. oc. Shaftside - vertical liner panels positioned into studs, vertical gypsum face boards attached to studs; floorside - vertical gypsum base boards attached to studs.

A. Vertical Shaft Wall Assembly; System F:

1. Based upon UofC 2-8-72 and 6-23-75, 2 hr estimated.  Framing - steel studs 24 in. oc.  Shaftside - vertical liner panels positioned into studs; floorside - horizontal resilient channels attached to studs, horizontal gypsum base boards attached to resilient channels, vertical gypsum face boards attached to resilient channels through base boards; inside - sound insulation friction-fit between studs.

A. Vertical Shaft Wall Assembly; System G:

1. Based upon UofC 2-16-72, 3 hr estimated.  Framing - steel studs 24 in. oc. Shaftside - vertical liner panels positioned into studs; floorside - vertical gypsum inner base boards attached to studs, horizontal outer base boards attached to studs through inner base boards, vertical gypsum  face boards attached to studs through inner base boards.

A. Vertical Shaft Wall Assembly; System H:

1. Based upon UofC 5-24-72, 4 hr estimated.  Framing - steel studs 24 in. oc.  Shaftside - vertical liner panels positioned into studs; floorside - vertical liner panels attached to studs, vertical gypsum inner base boards attached to studs through attached liner panels, horizontal furring channels attached to studs through inner base boards and attached liner panels, vertical gypsum outer base boards attached to furring channels, vertical gypsum face boards attached to furring channels through outer base boards.

A. Vertical Shaft Wall Vent Shaft Assembly; System  VA:

1. UL Design U505, 2 hr. Framing - steel perimeter angles and horizontal bracing angles.  Shaftside - vertical gypsum base boards attached to perimeter and bracing angles, floorside - vertical gypsum liner panels adhered to base boards, vertical gypsum face boards adhered to liner panels and attached to perimeter and bracing angles through liner panels.

1.05 SUBMITTALS

A. Follow Section 01340-Product Data, Shop Drawings, and Samples.

B. Product Data: Submit manufacturer's product specifications and installation instructions for systems shown.

C. Shop Drawings: Submit installation drawings which:

1. Show shaft wall dimensions relative to other work.

2. Locate all openings in shaft wall with details indicating special construction for work of other Sections and conformance with requirements of fire rated construction.

D. Certificates: Submit manufacturer's certification of compliance with fire and sound requirements for each system shown.  Include name of manufacturer and complete description of door frames, elevator door frames, electrical boxes, and other penetrations included in each tested assembly for each system shown.

1.06 QUALITY ASSURANCE

A. Single Source Responsibility: Provide steel framing, gypsum boards, insulation, fasteners, joint treatments, and other materials in the assembly or assemblies from the single manufacturer which has utilized these materials in recognized fire containment and sound tests.

1.07 DELIVERY, STORAGE, AND HANDLING

A. Follow Section 01610-Delivery, Storage, and Handling.

1.08 PROJECT CONDITIONS

A. Do no joint finishing when temperature in space being finished is less than 55oF (13oC).  Ventilation must be adequate to carry off excess moisture.

PART 2 PRODUCTS

2.01 MATERIALS

******** Select one or more of the following System paragraphs.  Select size(s).  Delete remaining [Systems] and System paragraphs. ********

A. Runners:

1. J-Runners; [System A], [System B], [System C], [System D], [System E], [System F], [System G], [System H], [System AA], [System AB], [System AC]: Galvanized steel; width and metal thickness (24 ga minimum) to accommodate adequately loads imposed from studs selected from stud manufacturer's published limiting height table; [212JR24], [212JR20], [400JR24], [400JR20], [600JR20]; lengths as required; ASTM C645; as supplied by USG.

1. Angle Runners and Bracing Angles; System VA: Galvanized steel; 1-1/4 in. x 3/4 in. x 22 ga; lengths as required; ASTM C645; as supplied by USG.

******** Use this for ALL Systems.  ********

B. Runner Fasteners:

1. Power-driven type; must withstand 193 lb single shear and 200 lb bearing force when driven into sill without exceeding allowable design stress in runner, fastener, or structural support.

******** Continue selections.  ********

C. Studs:

1. CH-Studs; [System A], [System B], [System E], [System F], [System G], [System H], [System AA], [System AB], [System AC]: Galvanized steel; width and metal thickness (25 ga minimum) as selected from stud manufacturer's published limiting height table; [212CH25], [212CH22], [212CH20], [400CH25], [400CH20], [600CH20]; unspliced lengths, as required, providing continuous edge support for liner board edges; ASTM C645; as supplied by USG.

1. CH-Studs; [System D]: Galvanized steel; width and metal thickness (20 ga minimum) as selected from stud manufacturer's published limiting height table; [212CH20], [400CH20], [600CH20]; unspliced lengths, as required, providing continuous edge support for liner board edges; ASTM C645; as supplied by USG.

1. CH Studs; [System C], [System VA]: Galvanized steel; width and metal thickness (25 ga minimum) as selected from stud manufacturer's published limiting height table; [400CH25], [400CH20], [600CH20]; unspliced lengths, as required, providing continuous edge support for liner board edges; ASTM C645; as supplied by USG.

2. E-Studs; [System A], [System B], [System E], [System F], [System G], [System H], [System AA], [System AB], [System AC], [System VA]: Galvanized steel; width and metal thickness (25 ga minimum) as selected from stud manufacturer's published limiting height table; [212ES25], [212ES22], [400ES25], [400ES20], [600ES25], [600ES20]; unspliced lengths, as required, providing continuous edge support for liner board edges; ASTM C645; as supplied by USG.

2. E-Studs; [System D]: Galvanized steel; width and metal thickness (20 ga minimum) as selected from stud manufacturer's published limiting height table; [212ES20], [400ES20], [600ES20]; unspliced lengths, as required, providing continuous edge support for liner board edges; ASTM C645; as supplied by USG.

2. E-Studs; [System C]: Galvanized steel; width and metal thickness (20 ga minimum) as selected from stud manufacturer's published limiting height table;  [400ES20], [600ES20]; unspliced lengths, as required, providing continuous edge support for liner board edges; ASTM C645; as supplied by USG.

******** Use the following for ALL Systems.  Select design load and deflection.  Delete remaining loads and deflections.  ********

D. Selection Criteria:

1. Stud, runner, and strut selection based upon:

a. Design load(s): Intermittent air pressure load as selected from stud manufacturer's published limiting height table; [5 psf], [7.5 psf], [10 psf], [15 psf].

b. Allowable deflection: As selected from stud manufacturer's published limiting height table; [L/120], [L/240], [L/360].

c. End reaction and bending stress: Do not exceed maximum allowable for given stud height.

2. Studs, runners, and struts must have the same, or greater, section properties as those used in the initial fire containment and sound tests.

******** Use the following for ALL Systems.  ********

E. Other Metal Components:

1. Jamb Struts: Galvanized steel, 20 ga; 3 in. back leg, same width as steel studs; lengths, as required; ASTM C 645; as supplied by USG.

2. Z-Clips: Galvanized steel; 16 ga x runner or stud width x stand-off distance x 1-1/2 in. each leg; ASTM A 446/A 446 M, A 525.

******** Continue selections.  ********

3. Resilient channels; System H: Galvanized steel, modified-hat shaped channel; 25 ga x 2-1/2 in. overall width x 1-1/2 in. face width x 1/2 in. depth; ASTM C645; RC-1 as supplied by USG.

******** Use this for ALL Systems.  ********

F. Gypsum Boards:

1. Liner panels: Gypsum panels; 1 in. thick x 24 in. wide x lengths as required; beveled edges, water resistant green face glass-mat; with UL Classification Label affixed; exceed ASTM C1658; SHEETROCK Brand Glass-Mat Liner Panels

******** Continue selections.  ********

2. Base boards; System D: Gypsum boards; 5/8 in. thick x 48 in. wide x lengths as required; tapered edges; with UL Classification Label affixed; ASTM C1396; FIRECODE Core, SHEETROCK Brand.

2. Base boards; [System B], [System F], [System AB], [System AC]: Gypsum boards; 1/2 in. thick x 48 in. wide x lengths as required; tapered edges; with UL Classification Label affixed; ASTM C1396; FIRECODE C Core, SHEETROCK Brand.

2. Base boards, [System G], [System H], [System VA]: Gypsum boards; 5/8 in. thick x 48 in. wide x lengths as required; tapered edges; with UL Classification Label affixed; ASTM C1396; FIRECODE C Core, SHEETROCK Brand.

3. Face boards, [System VA]: Gypsum boards; 5/8 in. thick x 48 in. wide x lengths as required; tapered edges; with UL Classification Label affixed; ASTM C1396; FIRECODE Core, SHEETROCK Brand.

3. Face boards, [System A], [System G], [System H], [System AA]: Gypsum boards; 5/8 in. thick x 48 in. wide x lengths as required; tapered edges; with UL Classification Label affixed; ASTM C1396; FIRECODE C Core, SHEETROCK Brand.

3. Face boards, [System B], [System E], [System F], [System AB], [System AC]: Gypsum boards; 1/2 in. thick x 48 in. wide x lengths as required; tapered edges; with UL Classification Label affixed; ASTM C1396; FIRECODE C Core, SHEETROCK Brand.

3. Face boards, System C: Gypsum boards; 3/4 in. thick x 48 in. wide x lengths as required; tapered edges; with UL Classification Label affixed; ASTM C1396; ULTRACODE Core, SHEETROCK Brand.

G. Cement Boards:

1. Face boards, System D: Aggregated portland cement board with polymer-coated, glass-fiber mesh embedded in front and back surfaces; 1/2 in. thick x 48 in. wide x 4' to 10' lengths as required; formed, smooth, reinforced edges; ASTM C1325, DUROCK Brand Cement Board.

H. Sound Insulation:

1. Blankets; System C: Paperless, semi-rigid spun mineral fiber mat, 3 in. thick; ASTM C665, Type I; THERMAFIBER Sound Attenuation Fire Blankets (SAFB).

1. Blankets; [System B], [System D], [System F]: Paperless, semi-rigid spun mineral fiber mat, 1-1/2 in. thick; ASTM C665, Type I; THERMAFIBER Sound Attenuation Fire Blankets (SAFB).

******** Use the following for ALL Systems.  ********

2.02 OTHER MATERIALS

A. Corner Reinforcement:

1. External corner reinforcement: Galvanized steel; 1-1/4 x 1-1/4 in., lengths as required; ASTM A653 Coating Designation Z90.; No.103, DUR-A-BEAD Brand.

B. Metal Trim:

1. L-shaped: Galvanized steel; 1/2 in., lengths as required; ASTM A653 Coating Designation Z90.; No. 200-B, SHEETROCK Brand.

C. Fasteners:

1. Steel framing: Steel screws; lengths as recommended by gypsum board products manufacturer; Type S, pan head; ASTM C1002.

2. Steel framing: Steel screws; lengths as recommended by gypsum board products manufacturer; Type S-12, pan head and low-profile head ASTM C954.

3. Gypsum board to steel framing: Steel screws; lengths as recommended by gypsum board products manufacturer, Type S-12 bugle head and pancake head; ASTM C954.

4. Gypsum board to resilient or furring channels: Steel screws; lengths as recommended by gypsum board products manufacturer, Type S-12 bugle head and pancake head; ASTM C954.

5. Cement board to steel framing: Steel screws; lengths as recommended by gypsum board products manufacturer; DUROCK Steel Screws.

******** Continue selections.  ********

D. Laminating Adhesive:

1. Joint compound; [System VA]: Vinyl based, without asbestos; ASTM C 475; SHEETROCK Brand All Purpose Joint Compound Ready-Mixed (ready-mixed drying type).

1. Adhesive; [System D]: Organic, Type 1; DUROCK Ceramic Tile Adhesive.

******** Use the following for ALL Systems.  ********

E. Joint Treatment:

1. Tape: High-strength fiber, 1-31/32 in. wide; ASTM C475; SHEETROCK Brand Joint Tape.

2. Taping compound: Vinyl based, without asbestos; ASTM C475; SHEETROCK Brand Taping Joint Compound Ready-Mixed (ready-mixed drying type).

3. Finishing compound: Vinyl based, without asbestos; ASTM C475; SHEETROCK Brand All Purpose Joint Compound (powder-mixed drying type).

4. Optional joint treatment materials: Other tapes, taping compounds, and finishing compounds may be used pursuant to gypsum board manufacturer's published recommendations.

F. Calk: Latex type; applied in accordance with ASTM C919; SHEETROCK Brand Acoustical Sealant.

2.03 MANUFACTURER:

A. United States Gypsum Company.

2.04 SUBSTITUTIONS

A. Products of other manufacturers will not be considered.

PART 3 EXECUTION

3.01 EXAMINATION

A. Examine locations to receive materials for conditions which will affect adversely installation.  Do not start materials installation until unsatisfactory conditions have been corrected.

3.02 PREPARATION

A. Field Dimensions: Verify location and dimensions where materials are to be installed.

B. Review shop drawings and coordinate work of other Sections which is integral with shaft wall installation.

******** If you wish a brief Part 3, use Articles 3.03 through 3.07.  If you wish a comprehensive Part 3, delete Articles 3.03 through 3.07 and continue with 3.08.  Don't forget to renumber the Articles.   ********

3.03 FRAMING INSTALLATION

A. Comply with gypsum products manufacturer's published instructions.

3.04 GYPSUM BOARD APPLICATION

A. Comply with gypsum products manufacturer's published instructions.

3.05 GYPSUM BOARD FINISHING

******** Select one or more of the following System paragraphs.  Delete remaining [Systems] and System paragraphs. ********

A. [System A], [System B], [System C], [System D], [System E], [System F], [System G], [System H], [System AA], [System AB], [System AC], [System VA]:

1. Level 1 as prescribed by ASTM C840.

A. [System A], [System B], [System C], [System D], [System E], [System F], [System G], [System H], [System AA], [System AB], [System AC], [System VA]:

1. Level 2 as prescribed by ASTM C840.

A. [System A], [System B], [System C], [System D], [System E], [System F], [System G], [System H], [System AA], [System AB], [System AC], [System VA]:

1. Level 3 as prescribed by ASTM C840.

A. [System A], [System B], [System C], [System D], [System E], [System F], [System G], [System H], [System AA], [System AB], [System AC], [System VA]:

1. Level 4 as prescribed by ASTM C840.

A. [System A], [System B], [System C], [System D], [System E], [System F], [System G], [System H], [System AA], [System AB], [System AC], [System VA]:

1. Level 5 as prescribed by ASTM C840.

3.06 CLEANING

A. Follow Section 01710-Final Cleaning.

3.07 PROTECTION

A. Protect the work from damage; repair to Architect's satisfaction or replace damaged materials.

END OF SECTION

******** END for brief Part 3  ********

******** Continue here for a comprehensive Part 3.   ********

******** Select for Systems A, B, C, D, E, F, G, H, and VA.  ********

3.08 VERTICAL WALL INSTALLATION

A. Runners, Studs, and Liner panels:

1. Attach J-Runners plumb with one another, long leg on shaftside, at floor and structure overhead using power-driven fasteners located 2 in. from each end and 24 in. oc between.  Cut jamb J-Runners or E-Studs not less than 3/8 in. nor more than 1/2 in. less than distance from floor to structure above.  Position J-Runners or E-Studs at wall structural jambs.  Do not attach to floor or overhead J-Runners.

2. With steel frame construction attach J-Runners to beams and J-Runners or E-Studs to columns prior to fireproofing application.  Where fireproofing is more than 1 in. thick, position Z-Clips at jambs no more than 4 in. from floor and structure above and no more than 24 in. oc between.  Attach Z-Clips to steel frame with power-driven fasteners.  Attach J-Runners and E-Studs to Z-Clips with two (2) 1/2 in. Type S-12 screws.  Remove excess fireproofing from insides of J-Runners and E-Studs before installing liner panels.

3. Cut liner panels 1 in. less than distance from floor to structure above; erect vertically into floor and overhead J-Runners, and into jamb J-Runner or E-Stud.  Where wall height exceeds maximum length of liner board, position board end joints within upper and lower 1/3 of height from floor to structure above; stagger joints in adjacent boards.  Achieve tight fit at mating board ends.

4. Cut C-H Studs not less than 3/8 in. nor more than 1/2 in. less than distance from floor to structure above.  Fit first C-H Stud over leading edge of first liner board.  Install remaining liner panels and C-H Studs.  Do not attach C-H Studs to J-Runners.

a. Do not splice C-H Studs or E-Studs.  For wall heights exceeding 16 ft attach C-H studs, E-Studs, or jamb J-runners to floor and overhead J-Runners with two (2) 1/2 in. Type S-12 screws on shaftside and one (1) on floorside.  Always fit liner panels tightly into studs or jamb runners.  Always fit studs or jamb runners tightly over liner panels.

5. Corners and intersections: Position jamb J-Runners or E-Studs at corners and T-intersections.

6. Door openings: Install E-Studs plumb at each jamb of swinging doors.  Install jamb struts plumb with long legs on shaftside at each jamb of elevator doors.  Attach jamb strut studs to floor and overhead J-Runners with two (2) 3/8 in. Type S-12 screws pan head on shaftside and one (1) on floorside.  Attach strut studs to door jamb anchors with two (2) 1/2 in. Type S-12 pan head screws per anchor.

a. For walls above doors miter-cut J-Runners legs and position J-Runner horizontally to fit tightly between strut studs to serve as opening head.  At each jamb extend J-Runner upward into overhead J-Runner.  Attach J-Runner webs to strut stud webs with 3/8 in. Type S-12 screws spaced not more than 12 in. oc, 2 in. above opening head, and not more than 4 in. from overhead J-Runner, using not less than 3 screws per jamb.  Install C-H Studs horizontally at not less than 24 in. oc; attach to each mitered jamb J-Runner one (1) 3/8" Type S-12 screw shaftside and one (1) floorside.

b. Provide additional liner panels, gypsum shims and fillers at elevator door frames as necessary to maintain fire integrity of the tested labeled frame construction.  Construct opening in conformance with frame manufacturer's fire test report; secure copy of fire test report from frame manufacturer and maintain on site for elevator inspector.

7. Small openings:   Frame openings with E-Studs or J-Runners at jambs; frame heads and sills with J-Runners.  Attach head and sill J-Runners to jambs with two (2) 3/8 in. Type S-12 screws on shaftside and one (1) on floorside.

8. Do not exceed allowable stresses in C-H Studs, E-studs or J-Runners.

******** Select for System H.  ********

B. Resilient Channels:

1. Position resilient channels at right angles to studs, spaced no more than 24 in. oc; attach to stud flanges with one (1) 3/8" Type S pan head screw driven through holes in channel mounting flange.  Install channels with mounting flange down.  Locate channels no more than 6 in. from floor and structure above.  Extend channels into corners and attach to corner framing.  Cantilever channel ends no more than 6 in.  Splice channels by lapping 3 in. directly over, and centered upon, a stud; screw attach through both flanges; drive one (1) additional screw at each end of lap.  Install 3 in. wide gypsum board filler strips below each channel at floor and above each channel at structure overhead.